## Submittal
Longsheng Pipeline Equipment Materials Co., Ltd.
EPDM Body Rubber Expansion Joint — Submittal
Flanged and threaded rubber expansion joints with EPDM cover and tube
Yellow cells = values to confirm before publishing (see cell comments). Clear the yellow fill afterwards.
Project
Project name
Contractor
Engineer
Tag / line no.
Quantity and sizes
Materials of construction
Cover (outer rubber) | EPDM
Tube (inner rubber) | EPDM
Reinforcement | Nylon / polyester tyre cord
Bead | Steel wire ring
Flanges | Q235 carbon steel, hot-dip galvanised / zinc plated / painted; SS304 or SS316L on request
Threaded unions | Malleable iron, galvanised; SS304 on request
Service limits
Temperature, continuous | -30 to +120 °C
Temperature, short periods | -50 to +150 °C
Pressure classes | PN10 · PN16 · PN25 (by size — see product datasheet)
Hydrostatic test | 1.5 × working pressure, every joint, no leakage or bulging
Vacuum | Per pressure class; vacuum support ring above the listed value
Media
Suitable (rating A) | Cold water, cooling water; Hot water to +80 °C; Hot water +80 to +120 °C; Seawater, brine; Sewage, wastewater; Chlorinated water (pools, ≤5 ppm); Phosphate-ester hydraulic fluid; Compressed air, oil-free; Sulphuric acid ≤ 10 %; Sulphuric acid 50–70 %; Hydrochloric acid ≤ 10 %; Phosphoric acid ≤ 85 %; Acetic acid ≤ 10 %; Caustic soda ≤ 50 %; Ammonia solution; Salt solutions; Acetone, MEK; Alcohols (ethanol, methanol); Ethylene glycol, antifreeze; Lime and cement slurry; FGD slurry (gypsum, chlorides)
Not suitable (rating X) | Mineral oil, lubricating oil; Hydraulic oil (mineral); Diesel, fuel oil; Gasoline (petrol); Crude oil; Kerosene, jet fuel; Natural gas; LPG, propane; Nitric acid over 30 %; Benzene, toluene, xylene
Full list | See Rubber Selection Chart, sheet "Chemical resistance"
Approval
Submitted by
Approved by
Date
Remarks
Longsheng Pipeline Equipment Materials Co., Ltd. · Tel / WhatsApp +86-15837196938 · sales1@lsruberjoint.com
Note on B17: Nylon or polyester? The double sphere page still has this marked to confirm.
Note on B20: SS304 unions — confirm you supply them.
Note on B23: Confirm against your compound recipe.
Note on B26: Confirm test factor (1.5×) and whether every joint is tested.