## Datasheet
Longsheng Pipeline Equipment Materials Co., Ltd. | [5 empty] | Tel / WhatsApp +86-15837196938 · sales1@lsruberjoint.com
Threaded Rubber Expansion Joint
Datasheet · DN15–DN50 (½"–2") · union ends, BSP or NPT
Yellow cells = values to confirm before publishing (see cell comments). Clear the yellow fill afterwards.
Materials of construction
1 | Rubber body |  | Twin sphere; EPDM standard, NBR for oily water
2 | Reinforcement |  | Nylon tyre cord
3 | Union nut |  | Malleable iron, galvanised; SS304 on request
4 | Union end |  | Malleable iron or SS304, female thread BSP or NPT
5 | Sealing lip |  | Rubber lip clamped by the nut — no separate gasket
Working conditions
Working pressure |  |  | 1.6 MPa
Burst pressure |  |  | 4.8 MPa
Temperature |  |  | −20 to +115 °C
Media |  |  | Water, hot water, air
Axial movement |  |  | 10 mm compression / 5 mm extension
Lateral / angular |  |  | 20 mm / 45°
Thread options
Type |  | Standard |  | Form | Angle | Seals on |  | Common in
G · BSPP |  | ISO 228-1 |  | Parallel | 55° | Gasket / O-ring |  | Europe, Middle East, Asia
R / Rc · BSPT |  | ISO 7-1 |  | Taper 1:16 | 55° | Thread + sealant |  | UK, Middle East, Africa, Asia
NPT |  | ASME B1.20.1 |  | Taper 1:16 | 60° | Thread + sealant |  | USA, Canada, Latin America
BSPT and NPT are not interchangeable: the thread angle differs, and from 1" up the pitch differs (11 vs 11½ threads per inch).
Dimensions and movement (mm)
DN | Inch | Length L |  | Axial compression | Axial extension | Lateral | Angular
|  | Type A | Type B
15 | ½" | 180 | 200 | 10 | 5 | 20 | 45°
20 | ¾" | 200 | 200 | 10 | 5 | 20 | 45°
25 | 1" | 210 | 200 | 10 | 5 | 20 | 45°
32 | 1¼" | 210 | 200 | 10 | 5 | 20 | 45°
40 | 1½" | 220 | 200 | 10 | 5 | 20 | 45°
50 | 2" | 220 | 200 | 10 | 5 | 20 | 45°
Type A / Type B: confirm what distinguishes the two lengths.
Reducing threaded joints (mm)
DN1 × DN2 | Inch | Length L | Axial compression | Axial extension | Lateral | Angular
20 × 15 | ¾" × ½" | 200 | 10 | 5 | 25 | 45°
25 × 20 | 1" × ¾" | 220 | 10 | 5 | 25 | 45°
32 × 25 | 1¼" × 1" | 220 | 10 | 5 | 25 | 45°
40 × 32 | 1½" × 1¼" | 240 | 10 | 5 | 25 | 45°
Face-to-face length can be made to fit an existing gap.
Order / submittal
Project / tag no.
Size and quantity
Pressure class
Rubber (cover / tube)
Thread type and union material
Options
Approved by / date
Longsheng Pipeline Equipment Materials Co., Ltd. · Tel / WhatsApp +86-15837196938 · sales1@lsruberjoint.com
Dahuai North Street, Xicun Village, Xicun Town, Gongyi City, Henan Province, China
Note on A38: Page marks A/B type difference as to confirm.
Note on D9: Marked "确认" on the web page — confirm material.
Note on D10: Marked "确认" on the web page — confirm material.
Note on D12: Marked "确认" on the web page — confirm material.